## RFI Register
MERIDIAN DATA CENTRE - PHASE 1 ¦ REQUEST FOR INFORMATION (RFI) REGISTER | [17 empty] | ReportDate
Source: EDMS export (Aconex-style) ¦ Register Report Date: 2026-07-20 ¦ Project No. MDC-P1 ¦ Ball-in-Court = party currently responsible for the next action | [17 empty] | 2026-07-20
RFI No. | Subject | Discipline | Status | Priority | Raised By | Ball-in-Court | Date Raised | Date Required | Date Closed | Days Open | Linked Activity | Spec Ref | Drawing Ref | Question | Proposed Solution / Response | Cost Impact (stated) | Schedule Impact (stated)
RFI-0001 | Confirmation of incoming utility fault level at 11 kV point of supply | Electrical | Closed | Medium | EPC Contractor | Owner | 2026-01-22 | 2026-02-05 | 2026-02-03 |  | ACT-004 | ELEC-6.1.1 | SLD-001 | Utility fault level required to finalise switchgear short-circuit rating. | Utility confirmed 25 kA at PoS; design retained. | None | None
RFI-0002 | Geotechnical bearing capacity clarification for foundation design | Civil | Closed | High | EPC Contractor | Consultant | 2026-01-28 | 2026-02-10 | 2026-02-09 |  | ACT-024 | CIVIL-2.1.1 | STR-014 | Allowable bearing pressure at pile-cap level to be confirmed. | Geotech report rev B issued; 220 kPa adopted. | None | None
RFI-0003 | UPS-02A installation clearances and cable entry orientation | Electrical | Open | High | EPC Contractor | Consultant | 2026-06-24 | 2026-07-15 |  |  | ACT-033 | ELEC-4.2.8 | ELE-220 | Front/side maintenance clearance vs room layout; bottom vs top cable entry for UPS-02A to be confirmed before installation proceeds. | Await Engineer mark-up of electrical room GA. | Potential - TBD | Potential - TBD
RFI-0004 | Chilled water design temperatures and delta-T confirmation | Mechanical | Closed | Medium | EPC Contractor | Consultant | 2026-02-14 | 2026-02-26 | 2026-02-24 |  | ACT-039 | MECH-4.2.1 | MEC-101 | Confirm CHW supply/return temperatures for pipe sizing. | 18/30 C confirmed; sizing retained. | None | None
RFI-0005 | Raised access floor panel load rating for high-density zone | Civil | Closed | Low | EPC Contractor | Consultant | 2026-03-03 | 2026-03-17 | 2026-03-14 |  | ACT-028 | CIVIL-2.2.1 | STR-045 | Confirm concentrated load rating for HD cabinets. | 5 kN/panel with 2.0 factor confirmed. | None | None
RFI-0006 | VESDA sampling pipe routing coordination with containment | Fire | Closed | Medium | EPC Contractor | Consultant | 2026-03-20 | 2026-04-02 | 2026-03-31 |  | ACT-038 | FIRE-2.1.1 | FIR-012 | Aspirating pipe routing clashes with cable containment in Hall A. | Rerouted per coordinated model; approved. | Minor - absorbed | None
RFI-0007 | UPS-02A retransfer / concurrent-maintainability test procedure basis | Commissioning | Open | High | Commissioning Agent | Consultant | 2026-06-30 | 2026-07-18 |  |  | ACT-046 | ELEC-4.2.2 | CX-UPS-02 | Confirm acceptance basis for inverter-to-bypass retransfer timing to be witnessed during UPS-02A commissioning; clarify pass criterion and instrumentation. | Await Engineer confirmation of test acceptance limits. | Potential - TBD | Potential - TBD
RFI-0008 | Generator exhaust routing and acoustic attenuation | Mechanical | Closed | Medium | EPC Contractor | Consultant | 2026-04-10 | 2026-04-24 | 2026-04-21 |  | ACT-032 | ELEC-5.1.2 | MEC-210 | Exhaust stack height and silencer selection for boundary noise. | Stack + residential silencer approved. | Minor - absorbed | None
RFI-0009 | MV switchgear arc-flash incident-energy labelling prior to energisation | Electrical | Open | High | EPC Contractor | Consultant | 2026-06-26 | 2026-07-16 |  |  | ACT-031 | ELEC-6.1.2 | ELE-060 | IEEE 1584 incident-energy study results and label schedule required before MV switchgear can be energised; confirm PPE category boundaries. | Await coordination study rev C and Engineer approval. | Potential - TBD | Potential - TBD
RFI-0010 | Structured cabling backbone fibre count and grade | IT | Closed | Low | EPC Contractor | Consultant | 2026-04-28 | 2026-05-12 | 2026-05-09 |  | ACT-036 | IT-2.1.1 | ITC-003 | Confirm OM4/OS2 counts for backbone pathways. | Counts confirmed per rev B; OS2 added. | None | None
RFI-0011 | Clean-agent cylinder room location and pressure relief venting | Fire | Closed | Medium | EPC Contractor | Consultant | 2026-05-05 | 2026-05-19 | 2026-05-16 |  | ACT-038 | FIRE-3.1.1 | FIR-030 | Relief vent sizing for protected volume to be confirmed. | Vent area confirmed per ISO 14520. | None | None
RFI-0012 | Generator bulk fuel storage tank capacity vs 48-hour autonomy | Mechanical | Open | High | EPC Contractor | Owner | 2026-07-02 | 2026-07-17 |  |  | ACT-032 | ELEC-5.1.3 | MEC-215 | Confirm bulk fuel tank sizing to demonstrate 48-hour autonomy at full standby load; verify available plot area for the required tank. | Await Owner decision on tank size / footprint. | Potential - significant | Potential - TBD
RFI-0013 | Earthing electrode arrangement to achieve 1 ohm target | Electrical | Closed | Medium | EPC Contractor | Consultant | 2026-05-22 | 2026-06-04 | 2026-06-02 |  | ACT-037 | ELEC-6.3.1 | ELE-090 | Electrode count/spacing to meet 1 ohm given soil resistivity. | Additional rods approved; target met in design. | Minor - absorbed | None
RFI-0014 | CRAH condensate drainage routing in data hall | Mechanical | Closed | Low | EPC Contractor | Consultant | 2026-06-01 | 2026-06-15 | 2026-06-12 |  | ACT-041 | MECH-4.1.1 | MEC-130 | Condensate drain routing under raised floor to be confirmed. | Routing approved; trace heating added. | None | None
RFI-0015 | PDU output configuration and breaker schedule confirmation | Electrical | Closed | Medium | EPC Contractor | Consultant | 2026-06-10 | 2026-06-24 | 2026-06-20 |  | ACT-035 | ELEC-6.2.1 | ELE-150 | Confirm PDU output breaker schedule for busway taps. | Schedule confirmed per rev B. | None | None
Total RFIs
Open
Closed